## 1. Table_of_Contents
Table of Contents
Sheet # | Sheet Name | Table Name | Sheet Description
Sheet 2 | Quantum_System_Configuration | Table S1: Modeled quantum system configurations | Describes the system paramters for the three modeled quantum system configurations
Sheet 3 | Energy_Resource_Calculations | Table S2: Energy and resource calculations for quantum systems | Presents detailed calculations for modeled quantum system configurations in Sheet 2
Sheet 4 | Energy_Resource_Quant_Summary | Table S3: Summary of energy and resource usage for quantum systems | Summarizes the energy and resource consumption of modeled quantum systems in Sheet 3
Sheet 5 | Future_Quantum_Scaling | Table S4: Inputs and assumptions for future scaling of QuACI Table S5: Energy and resource impacts of future scaling of QuACI | Presents calculations on energy and resource impacts of integration of quantum systems with advanced classical computing and digital infrastructure
Sheet 6 | References | Table S5: List of references | List of references noted in this spreadsheet
Citation
Authors
Acknowledgements
Disclaimer: This sheet is password protected to prevent any accidental changes to calculations. To unprotect/unlock the sheet, use the following password: QUEENS@ORNL.
NS: Not protected as of now. Do before submission/finalization.
Key Abbreviations
DR | dilution refrigerator
FTQC | fault tolerant quantum computer
K | Kelvin
kW | kilowatts
mK | milliKelvin
MW | megawatts
PQ | physical qubit
RSA | Rivest-Shamir-Adleman cryptosystem
QuACI | Quantum Accelerated Computing Infrastructure
This work has received funding from the University of Tennessee – Oak Ridge Innovation Institute (UT-ORII). The views expressed represent the authors alone, and do not necessarily reflect those of Oak Ridge National Laboratory, U.S. Department of Energy, or University of Tennessee. We thank the following ORNL colleagues for advice and support over the course of this study: Dave Rasmussen, Chris Marcus, Ketan Choukekar, AB Siddik, Adam Carroll, Travis Humble, Warren Grice, Nick Peters, Bronson Messer, Jim Rogers, Woong Shin, Colby Earles, Jeremy Busby, Jacob Morris, Steve Peterson, Terri Cleveland, Rian Lewis, Mark Connell, Rob Crowell, Claire Marvinney, David Sholl, Kate Evans, Grace Martinez, Anna Galyon. In addition, we thank the following colleagues within the community: Charles Sims (UTK), Marianne Wanamaker (UTK), Greg Tatkowski (Fermilab), Robert Goodin (USGS), Clay Almy (Global Quantum Intelligence), Bill Halperin (Northwestern University), Mark Elsesser (American Physical Society), Moses Chan (Pennsylvania State University), Billy Roberts (NREL), Arman Shehabi (LBNL), Eric Masanet (UC Berkeley), Tom Wilson (EPRI), Joe Keefe (Ostergaard Acoustical Associates), Joseph Horesco (Acentech), Ralph T. Muehleisen (ANL), and Laura Appenzeller (UIUC).
McCollum et al., (2026). Energy and Physical Resource Impacts of Quantum Computing at Scale. JOURNAL NAME. DOI/ISSUE/VOLUME/PAGE NUMBER (TBD)
David McCollum, Soumendra Bhanja, Sarah Chehade, Andrea Delgado, Melrose Pan, Naushita Sharma, Weijun Yao (NS: Kept same as the Commentary Paper, Author order as surnames in alphabetical order. Please change as necessary.)

## 2. Quantum_System_Configuration
Table S1: Modeled quantum system configurations
Quantum System Configuration → | Practical FTQC | Small FTQC | Large FTQC | Notes & Documentation
Example Base Designs → System Parameters ↓ | IBM's System Two (2027+) | IBM's System Two (2033+) | IBM System Two (2033+) scaled to Fermilab's Colossus**, then with improved error correction and higher qubit density
# of logical qubits | 200 | 2000 | 5000 | FTQC needs at least 100 logical qubits, and more likely at least 1,000. Solving complex chemical simulations requires 4,000 or more. IBM's Blue Jay system planned for the 2033+ timeframe claims 2,000 logical qubits, 1 billion gates, advanced error-correction and full fault-tolerance. | Schematic for resource consumption flow paths for a FTQC
Ratio of physical to logical qubits | 500 | 1000 | 2000 | Values for physical-to-logical qubit ratio of between 500 and 2,000 are reasonable to assume for future FTQC systems at varying levels of error rate, and therefore functionality. Based on Ezratty (2024), Fig. 253, p. 291, and on the best-practices being designed and explored by Google, IBM, and others.
Logical qubit error rate | around 10^-7 | around 10^-12 | around 10^-15 | See Ezratty (2024), Fig. 253, p. 291. According to text on p. 295, an error rate of 10^-15 is needed for RSA-2048 key encryption, and lower for solving complex chemical simulations. These values do not feed into any calculations - for reference purpose only.
# of physical qubits (base level) | 100000 | 2000000 | 10000000 | -
Additional # of physical qubits needed for error-correction | 100000 | 2000000 | 10000000 | Upon discussion with quantum computing experts, the number of physical qubits needed for error-correction is assumed to be equal to the previously calculated number of physical qubits (i.e., 2x the base level of physical qubits). This assumes surface-code style algorithms for error correction, which could potentially improve markedly in the future -- an intense area of research at present.
Total physical qubits needed | 200000 | 4000000 | 20000000 | -
Volume of cryo-chamber (m^3) | 1.7 | 1.7 | 5 | From IBM's reporting, each System Two (Practical and Small FTQC) "cluster" (including 3 dilution refrigerators inside) has a working volume of 1.7 m^3. Fermilab's Colossus (Large FTQC) has a volume of 5.0 m^3 (with 12 dilution refrigerators inside; 10 of them at 20 mK). For cryo-coolers, reference design is based on the Bluefors/Cryomech PT415 unit with a CPA1110 compressor. (https://bluefors.com/products/pulse-tube-cryocoolers/pt415-pulse-tube-cryocooler. Current as of 09/15/2025). For nitrogen and helium liquefaction, reference design is based on the Linde L1610 unit with a 2RS compressor. Based on discussion with cryogenics experts, a L1610 helium liquefier will be able to support the Colossus sized quantum system, i.e., 12 LD400 DRs. (https://assets.linde.com/-/media/global/kryotechnik/kryotechnik/products/datasheet-l1610-lr1630-helium-liquefier-refrigerator.pdf. Current as of 09/15/2025). For dilution refrigerators, reference design is based on the Bluefors LD400 unit. (https://bluefors.com/products/dilution-refrigerator-measurement-systems/ld-dilution-refrigerator-measurement-system/. Current as 09/15/2025). Electricity consumption includes pumping, compression, liquefaction, and slow control systems used for monitoring. In all cases, the lowest temperature achieved within the dilution refrigerators is 10-20 milliKelvin. This is the qubit working temperature.
# of physical qubits per cryo-chamber | 3240 | 25000 | 1200000 | For Practical FTQC, assume that it becomes too challenging to move beyond 1,080 physical qubits per dilution refrigerator (= 9 x 120 qubits per Nighthawk chip). This is similar to Fujitsu's target for the late-2020s (= 1,024 qubits per dilution refrigerator). Each of IBM's System Two clusters (Small FTQC) has 3 DRs; the plan in 2033+ is that each of these clusters will support 25,000 physical qubits = 8,333 physical qubits per dilution fridge. For the Large FTQC, use the value of 120,000 physical qubits per DR from Mohseni et al. (2025); see the caption to Figure 27 of the paper. See Ezratty (2024), p. 415, and IBM's "2025 Development & Innovation Roadmap", for the the IBM numbers. See Fujitsu's "Fujitsu Quantum Computing Strategy (April 2025)" for their expectations.
# of 20-mK dilution refrigerators per cryo-chamber | 3 | 3 | 10 | See note in cell above for the discussion on IBM's System Two (Practical & Small FTQC). See Hollister et al. (2024) for the information on Colossus (Large FTQC); there are 12 dilution refrigerators, but 2 of them operate at higher temperatures (hence, 12-2 = 10 DRs).
# of physical qubits per 20-mK dilution refrigerator | 1080 | 8333.3333 | 120000 | See above notes.
# of cryo-chambers | 61.7284 | 160 | 16.6667 | -
# of dilution refrigerators | 185.1852 | 480 | 166.6667 | -
Energy consumption of cryo-chamber (kW) | 105 | 105 | 112 | See Ezratty (2024), p. 338. Each of IBM's System Two clusters (Practical and Small FTQC) has 3 dilution refrigerators, and the cluster consumes 105 kW. Estimate for Small FTQC takes its 40,000 kW of electricity consumption for a cooling power of 75 kW @ 4.5 K (based on the ITER nuclear fusion facility) and then proportionally (linearly) downscales it to the size of Colossus (0.2 kW @ 5 K). Estimates for Large FTQC power consumption are derived for a system that uses a cryogenics plant (as with Colossus) instead of pulse-tube cryo-coolers.
Legend for Numerical values in Columns C, D, and E
Assumption (reference and inference provided in Column F)
Calculated Value
** Colossus refers to Fermilab's experimental cryoplant + cryo-chamber system (not xAI's supercomputer in Memphis, Tennessee, USA).

## 3. Energy_Resource_Calculations
Table S2: Energy and resource calculations for quantum systems
Parameter | Unit | Constants | Unit for Constants | Practical FTQC | Small FTQC | Large FTQC | Notes & Documentation
INPUTS (Control Variables / Base Assumptions)
Computing
Physical Qubits per Logical Qubit | - |  |  | 500 | 1000 | 2000
Logical Qubits | qubit |  |  | 200 | 2000 | 5000
Time | hours |  |  | 8760 | 8760 | 8760
Cryogenics
Energy consumption of cryo-chamber | kW |  |  | 105 | 105 | 112
Volume of cryo-chamber | m^3 |  |  | 1.7 | 1.7 | 5
# of 20- K dilution refrigerators per cryo-chamber |  |  |  | 3 | 3 | 10
PQ / Cryochamber |  |  |  | 3240 | 25000 | 1200000
Control Electronics
| W/qubit |  |  | 5 | 0.0052 | 0.0052 | Potocnik et al. (2025) cites Yoo et al. (2023) value of 5 W/qubit. This is consistent with control electronics operating at room temperatures. According to Geck et al. (2025) on p. 2: “The power consumption per qubit for the spin qubit controllers is estimated to be in the range of 1.7 - 5.2mW/qubit with a frequency spacing between 31.3-125 MHz. All electronics are placed at 3-4 K.” Yoo et al. (2023) – also say that < 4 mW/qubit is possible when the control electronics are located in the cryogenic chamber and at temperatures of 3 K. Their higher value of 5 W/qubit is for control electronics located in room temperature environment. Thus, assume a higher value of 5 W/qubit for less optimistic cases (this is consistent with situating control electronics outside cryo-chamber and thus operating at room temperature). Then, assume lower value of 0.0052 W/qubit for more optimistic cases (this is consistent with situating control electronics inside cryo-chamber and thus operating at temperatures of 3-4 K).
CALCULATED PARAMETERS
Computing
Physical Qubits (total, including error correction) | Qubit | 2 |  | 200000 | 4000000 | 20000000
Cryogenics
# of physical qubits per 20-mK dilution refrigerator |  |  |  | 1080 | 8333.3333 | 120000
# Cryochambers |  |  |  | 61.7284 | 160 | 16.6667
# DR |  |  |  | 185.1852 | 480 | 166.6667
ELECTRIC POWER CONSUMPTION
Control electronics | kW |  |  | 1000 | 20.8 | 104
Cryogenics | kW |  |  | 6481.4815 | 16800 | 1866.6667
Cryochamber (W/PQ) | W/PQ |  |  | 32.4074 | 4.2 | 0.093333
Cooling water circulation | kW |  |  | 2466 | 5754 | 1644
Baseload | kW | 0.1 |  | 994.7481 | 2257.48 | 361.4667 | Assumed 10% of the total power consumption.
Miscellaneous | kW | 0.1 |  | 994.7481 | 2257.48 | 361.4667 | Micellaneous power consumption is from lighting, heating, ventilation, and cooling requirements of the buildings themselves (not the computing equipment). Assumed 10% of the total power consumption. DOE (2015). An assessment of energy technologies and research opportunities. Quadrennial Technology Review. United States Department of Energy, 12-19. (https://www.energy.gov/sites/prod/files/2017/03/f34/qtr-2015-chapter5.pdf#page=3.18) Lighting: https://www.eia.gov/tools/faqs/faq.php?id=99&t=3
Total Power Consumption | kW |  |  | 11936.9778 | 27089.76 | 4337.6
Power consumption per Physical Qubit | W/Qubit |  |  | 59.6849 | 6.7724 | 0.21688
Annual Electricity Consumption | MWh |  |  | 104567.9253 | 237306.2976 | 37997.376
COOLING WATER CIRCULATION
Helium Liquefier (achieving ~4K) | gal/min | 15 |  | 925.9259 | 2400 | 250 | Assuming Linde L1610 Liquefier with RSS Compressor, that is water cooled, 15 gpm at 75 deg F max and 45 psig supply pressure (57 lpm at 24 deg C and 310 kPa). Reference: https://assets.linde.com/-/media/global/kryotechnik/kryotechnik/products/datasheet-l1610-lr1630-helium-liquefier-refrigerator.pdf
Pulsetube cryocooler (achieving 2K) | gal/min | 3 |  | 555.5556 | 1440 | 500 | Assuming Bluefors/Cryomech PT415 Pulse Tube Cryocooler @ 3 gal/min. Reference: https://bluefors.com/products/pulse-tube-cryocoolers/pt415-pulse-tube-cryocooler/
Total | gal/min |  |  | 1481.4815 | 3840 | 750
Chiller Calcs
Incoming Temperature | deg F | 55.4 |  |  |  |  | Based on private conversations with experts who have previously conducted an analysis of cooling water needs for a potential quantum facility in the U.S. Also, agrees with the note in Row 33 for the helium liquefier.
Outgoing Temperature | deg F | 39.2 |  |  |  |  | Based on private conversations with experts who have previously conducted an analysis of cooling water needs for a potential quantum facility in the U.S.
Sizing Factor |  | 1.2 |  |  |  |  | Typically, chillers are oversized by 20% for safety margin.
Calculated Chiller capacity | ton |  |  | 1500 | 3500 | 1000 | Chiller tonnage (nameplate) is in 500 ton increments. Reference: Table 3 from USEPA (2017). https://www.epa.gov/sites/default/files/2017-12/documents/ws-commercialbuildings-waterscore-mechanical-systems-guide.pdf. Chiller sizing calculations based on: https://waterchillers.com/chiller-resources/sizing-information/.
Chiller Energy Consumption | kW | 0.47 | kW/ton | 705 | 1645 | 470 | Assuming best available tonnage for water-cooled chillers at 0.47 kW/ton. Reference: https://www.deq.nc.gov/environmental-assistance-and-customer-service/ias-energy-efficiency/opportunities/chillers/download
Annual Water Consumption | Mgal | 1.8 |  | 11.826 | 27.594 | 7.884 | Consumptive water is at the cooling tower that supplies water to the chillers. Approximately 1.8 gallons of water are evaporated (consumed/lost) at cooling towers for every ton-hour of cooling provided by the chillers, regardless of tower efficiency. Industrial chillers operate typically at 50% load. Reference: USEPA (2017). Water Efficiency Management Guide. Mechanical Systems. https://www.epa.gov/sites/default/files/2017-12/documents/ws-commercialbuildings-waterscore-mechanical-systems-guide.pdf. Accessed on 09/15/2025.
Water Requirement | MGD | 365 | days | 0.0324 | 0.0756 | 0.0216 | "million gallons per day (MGD)" is common unit for potable water supply design estimates.
Electricity for water supply | kWh | 1000 | kWh/Mgal | 1350 | 3150 | 900 | Electricity used for distribution and pumping from a water source to a QuACI facility. Reference for electricity use for finished water pumping to end users ~ 67% of total energy as noted in (Ehrhard, R., & Murphy, J. (2009). Driving energy efficiency in the US Water & Wastewater industry by focusing on operating and maintenance cost reductions. Energy, 25, 40.) USEPA notes 700-1200 kWh/Mgal for distribution (https://www.epa.gov/sites/default/files/2015-08/documents/wastewater-guide.pdf. Current as of 09/15/2025).
Water Use Effectivenes for Quantum Centers | l/kWh |  |  | 0.42811 | 0.44017 | 0.78543 | For reference, comparing with current data centers range of 0.7 - 1.5 liters/kWh (Lei et al. 2025).
Total Cooling Water Circulation Power | kW |  |  | 2466 | 5754 | 1644
Annual electricity for water supply | kWh |  |  | 21602160 | 50405040 | 14401440
Nitrogen
Cooling of the 80K shield | million liters per year (gas at 0 °C and 1 atm) | 0.83333 |  | 873.837 | 2264.9856 | 786.4533 | Liquid nitrogen is used for the cooling of the 80K shield. The typical budget is the range of 10-15 liters/hr for a Colossus style system (~12 DRs).
Cryogenic plant (liquefier) | million liters per year (gas at 0 °C and 1 atm) | 4.1667 |  | 4369.1852 | 11324.928 | 3932.2667 | Achieving efficient helium liquefaction is preferable with liquid nitrogen pre-cooling . Based on discussion with cryogen expert, typical L1610 helium liquefier operates at ~50 liter/hour for 12 DRs (Colossus sized system) at STP conditions.
Total | million liters per year (gas at 0 °C and 1 atm) |  |  | 5243.0222 | 13589.9136 | 4718.72
Helium-4 and Helium-3
4He (stock/inventory) | liters (liquid at -269 °C) | 83.3333 | liters/DR | 15432.0988 | 40000 | 13888.8889 | Helium-4 is contained in storage dewars and circulated in closed loop in the L1610 helium liquefier to reach necessary 4-5K refrigerator temperatures. Based on collaborations with cryogenics experts, a 1000 L helium-4 storage dewar can support the operation of L1610. Additonally, a L1610 helium liquefier will be able to support the Colossus sized quantum system, i.e., 12 LD400 DRs. The helium-4 storage dewar has a typical pressure maintained is between 3 psig tp 30 psig.
3He (stock/inventory) | liters (gas at 0 °C and 1 atm) | 18 | liters/DR | 3333.3333 | 8640 | 3000 | The current Bluefors LD400 design uses 18 liters per DR.
Additional Constants
Expansion ratio converting 1 liter of cryo-liquid to 1 liter of gas at STP (0 deg C and 1 atm) | Value | Reference
Nitrogen | 646.4 | https://www.uigi.com/calculators/nitrogen-quantity-conversions-calculator/
Helium-4 | 697 | https://brainly.com/question/32202339

## 4.Energy_Resource_Quant_Summary
Table S3: Summary of energy and resource usage for quantum systems
Parameter | Unit | Practical FTQC | Small FTQC | Large FTQC
Physical Qubits | # | 200000 | 4000000 | 20000000
Electricity Consumption
Control Electronics | kW | 1000 | 20.8 | 104
Cryogenics | kW | 6481.4815 | 16800 | 1866.6667
Cooling Water Circulation | kW | 2466 | 5754 | 1644
Baseload IT | kW | 994.7481 | 2257.48 | 361.4667
Miscellaneous | kW | 994.7481 | 2257.48 | 361.4667
Total | MW | 11.937 | 27.0898 | 4.3376
Per Unit
Control Electronics | W/qubit | 5 | 0.0052 | 0.0052
Cryogenics | W/qubit | 32.4074 | 4.2 | 0.093333
Cooling Water Circulation | W/qubit | 12.33 | 1.4385 | 0.0822
Baseload IT | W/qubit | 4.9737 | 0.56437 | 0.018073
Miscellaneous | W/qubit | 4.9737 | 0.56437 | 0.018073
Total | W/qubit | 59.6849 | 6.7724 | 0.21688
% Contribution
Control Electronics | % | 8.377% | 0.07678% | 2.398%
Cryogenics | % | 54.3% | 62.02% | 43.03%
Cooling Water Circulation | % | 20.66% | 21.24% | 37.9%
Baseload IT | % | 8.333% | 8.333% | 8.333%
Miscellaneous | % | 8.333% | 8.333% | 8.333%
Total | % | 100% | 100% | 100%
Resource Consumption
Nitrogen | million liters per year (gas at 0 °C and 1 atm) | 5243.0222 | 13589.9136 | 4718.72
3He | liters (gas at 0 °C and 1 atm) (stock/inventory) | 3333.3333 | 8640 | 3000
4He | liters (liquid at -269 °C) (stock/inventory) | 15432.0988 | 40000 | 13888.8889
Water | million liters per year | 44.7663 | 104.4547 | 29.8442
Water | million gallons per day | 0.0324 | 0.0756 | 0.0216

## 5. Future_Quantum_Scaling
Table S4: Inputs and assumptions for future scaling of QuACI
Inputs and Assumptions | Values | Notes & Documentation |  |  |  | Legend for Numerical values in Table S4 |  | Graphs
Base year | 2025 | Most recent statistics on U.S. data centers are available in this year. |  |  |  | Assumption (reference and inference provided in cells labeled as "Notes") |  | Electric Power | Water
Future year | 2045 | Representative future year in the 2040s |  |  |  | Calculated Value
# Advanced data centers | 68 | Advanced data centers include "Datacenter type" labeled as "Cloud", "Crypto Mining", "Hyperscale" from the S&P Global Data that were built solely in 2024. |  |  |  | Notes
# Hyper-scalar data centers/yr | 75 | Assumed based on S&P Global Data's 68 new data centers in 2024 and 74 (54% of 137 new data centers in the USA as of March 2025, Synergy Research Group as of March 2025; https://www.srgresearch.com/articles/hyperscale-data-center-count-hits-1136-average-size-increases-us-accounts-for-54-of-total-capacity)
2045 Scenario 1: Low penetration of QuACI | 10% | Assuming 10% of advanced digital infrastructure built between 2026 and 2045 will have some variant of FTQC modeled in Sheet 2.
2045 Scenario 2: High penetration of QuACI | 100% | Assuming 100% of advanced digital infrastructure built between 2026 and 2045 will have some variant of FTQC modeled in Sheet 2.
FTQC mix in 2045 QuACI | Mix 1 | Mix 2 | Mix 3 | Notes
Practical FTQC | 100% | 0% | 0% | Mixes define the combined deployment of Practical, Small FTQC, and Large FTQC for a future scenario.
Small FTQC | 0% | 100% | 0% |  |  |  |  | Liquid Nitrogen | Liquid Helium-4
Large FTQC | 0% | 0% | 100%
Possible digital infrastructure in 2040s | Values | Notes
# Advanced data centers | 1500 | Typically, systems are designed to have redundant (or backup) equipment to assist with production downtime (intentional and/or unexpected). We assume the availability of at least one additional QuACI system (2N redundancy) for risk tolerance. As with other existing computing infrastructure, a future well integrated QuACI will have the capability to transfer computing tasks to network-connected QuACIs (if low latency) to help with efficient operations.
# QuACI in 2045 Scenario 1 | 150
# QuACI in 2045 Scenario 2 | 1500
Scenario 1 FTQC mix in 2045 QuACI | Mix 1 | Mix 2 | Mix 3 | # Redundant facilities
Practical FTQC | 150 | 0 | 0 | 2
Small FTQC | 0 | 150 | 0 | 2
Large FTQC | 0 | 0 | 150 | 2
Scenario 2 FTQC mix in 2045 QuACI | Mix 1 | Mix 2 | Mix 3 | # Redundant facilities
Practical FTQC | 1500 | 0 | 0 | 2
FTQC (Small) | 0 | 1500 | 0 | 2 |  |  |  | Isotope Helium-3 |  |  |  | AI Data Centers | Quantum Accelerated Computing Infrastructure (QuACI)
FTQC (Large) | 0 | 0 | 1500 | 2 | [6 empty] | 2025 | 359 | 0
[10 empty] | 2045 | Low Penetration | 1350 | 150
Table S5: Energy and resource impacts of future scaling of QuACI | [10 empty] | High Penetration | 0 | 1500
Parameter | Unit | Mix 1 | Mix 2 | Mix 3 | Mix 1 | Mix 2 | Mix 3
|  | Low Penetration |  |  | High Penetration
Physical Qubits | # | 60000000 | 1200000000 | 6000000000 | 600000000 | 12000000000 | 60000000000
Practical FTQC | # | 60000000 | 0 | 0 | 600000000 | 0 | 0
Small FTQC | # | 0 | 1200000000 | 0 | 0 | 12000000000 | 0
Large FTQC | # | 0 | 0 | 6000000000 | 0 | 0 | 60000000000
Electric Power Consumption | GW | 3.5811 | 8.1269 | 1.3013 | 35.8109 | 81.2693 | 13.0128
Practical FTQC | GW | 3.5811 | 0 | 0 | 35.8109 | 0 | 0
Small FTQC | GW | 0 | 8.1269 | 0 | 0 | 81.2693 | 0
Large FTQC | GW | 0 | 0 | 1.3013 | 0 | 0 | 13.0128
Other Resources
Nitrogen | million liters per year (gas at 0 °C and 1 atm) | 1572906.6667 | 4076974.08 | 1415616 | 15729066.6667 | 40769740.8 | 14156160
Practical FTQC | million liters per year (gas at 0 °C and 1 atm) | 1572906.6667 | 0 | 0 | 15729066.6667 | 0 | 0
Small FTQC | million liters per year (gas at 0 °C and 1 atm) | 0 | 4076974.08 | 0 | 0 | 40769740.8 | 0
Large FTQC | million liters per year (gas at 0 °C and 1 atm) | 0 | 0 | 1415616 | 0 | 0 | 14156160
3He | liters (gas at 0 °C and 1 atm) | 1000000 | 2592000 | 900000 | 10000000 | 25920000 | 9000000
Practical FTQC | liters (gas at 0 °C and 1 atm) | 1000000 | 0 | 0 | 10000000 | 0 | 0
Small FTQC | liters (gas at 0 °C and 1 atm) | 0 | 2592000 | 0 | 0 | 25920000 | 0
Large FTQC | liters (gas at 0 °C and 1 atm) | 0 | 0 | 900000 | 0 | 0 | 9000000
4He | liters (liquid at -269 °C) | 4629629.6296 | 12000000 | 4166666.6667 | 46296296.2963 | 120000000 | 41666666.6667
Practical FTQC | liters (liquid at -269 °C) | 4629629.6296 | 0 | 0 | 46296296.2963 | 0 | 0
Small FTQC | liters (liquid at -269 °C) | 0 | 12000000 | 0 | 0 | 120000000 | 0
Large FTQC | liters (liquid at -269 °C) | 0 | 0 | 4166666.6667 | 0 | 0 | 41666666.6667
Water | million liters per year | 13429.8839 | 31336.3958 | 8953.256 | 134298.8393 | 313363.9583 | 89532.5595
Practical FTQC | million liters per day | 13429.8839 | 0 | 0 | 134298.8393 | 0 | 0
Small FTQC | million liters per day | 0 | 31336.3958 | 0 | 0 | 313363.9583 | 0
Large FTQC | million liters per day | 0 | 0 | 8953.256 | 0 | 0 | 89532.5595
Water | million gallons per day | 9.72 | 22.68 | 6.48 | 97.2 | 226.8 | 64.8

## 6. References
References
1 | CoreSite. 2025. “What Is Data Center Redundancy? N, N+1, 2N, 2N+1.” https://www.coresite.com/blog/data-center-redundancy-n-1-vs-2n-1.
2 | DOE. 2015. An Assessment of Energy Technologies and Research Opportunities. Quadrennial Technology Review. United States Department of Energy. https://www.energy.gov/sites/prod/files/2017/03/f34/qtr-2015-chapter5.pdf#page=2.27.
3 | Ezratty, Olivier. 2024. Understanding Quantum Technologies 2024. https://www.oezratty.net/wordpress/2024/understanding-quantum-technologies-2024/.
4 | Hollister, Matthew I, Ram C Dhuley, Christopher James, and Grzegorz L Tatkowski. 2024. “An Update on the Colossus mK Platform at Fermilab.” IOP Conference Series: Materials Science and Engineering 1302 (1): 012030. https://doi.org/10.1088/1757-899X/1302/1/012030.
5 | IBM. 2025. “IBM Quantum Roadmap.” https://www.ibm.com/roadmaps/quantum/2030/www.ibm.com/roadmaps/quantum/2030.
6 | James, C., M. Hollister, G. Tatkowski, and R. Dhuley. 2023. “Helium-3 Piping and Gas Handling Implementation for the Colossus Milli-Kelvin Platform at Fermilab.” Fermilab. https://lss.fnal.gov/archive/2023/poster/fermilab-poster-23-007-sqms.pdf.
7 | Lei, Nuoa, Jun Lu, Arman Shehabi, and Eric Masanet. 2025. “The Water Use of Data Center Workloads: A Review and Assessment of Key Determinants.” Resources, Conservation and Recycling 219 (June): 108310. https://doi.org/10.1016/j.resconrec.2025.108310.
8 | Mohseni, Masoud, Artur Scherer, K. Grace Johnson, et al. 2025. “How to Build a Quantum Supercomputer: Scaling from Hundreds to Millions of Qubits.” arXiv:2411.10406. Preprint, arXiv, January 31. https://doi.org/10.48550/arXiv.2411.10406.
9 | Potočnik, Anton. 2025. “How to Scale the Electronic Control Systems of a Quantum Computer.” Nature Electronics 8 (1): 3–4. https://doi.org/10.1038/s41928-024-01331-9.
10 | S&P Global Market Intelligence. 2025. “Datacenter KnowledgeBase: Q4 2024 Update.”
11 | Yoo, Juhwan, Zijun Chen, Frank Arute, et al. 2023. “34.2 A 28-Nm Bulk-CMOS IC for Full Control of a Superconducting Quantum Processor Unit-Cell.” 2023 IEEE International Solid-State Circuits Conference (ISSCC), February, 506–8. https://doi.org/10.1109/ISSCC42615.2023.10067292.
12 | Ehrhard, R., & Murphy, J. (2009). Driving energy efficiency in the US Water & Wastewater industry by focusing on operating and maintenance cost reductions. Energy, 25, 40.
System Design References from Vendor (Current as of 09/15/2025)
1 | Bluefors LD400 Dilution Refrigerator. https://bluefors.com/products/dilution-refrigerator-measurement-systems/ld-dilution-refrigerator-measurement-system/.
2 | PT415 Pulse Tube Cryocooler. https://bluefors.com/products/pulse-tube-cryocoolers/pt415-pulse-tube-cryocooler/
3 | Linde L161 helium liquefier/refrigerator. https://assets.linde.com/-/media/global/kryotechnik/kryotechnik/products/datasheet-l1610-lr1630-helium-liquefier-refrigerator.pdf
General Note: All webpage links noted in the entire excel workobook are active links as of 09/15/2025.